UCS TECHNICAL FIELD GUIDE

Connected-Building Technology Guide

NiagaraMods Reflow · Neeve AI · Blue Ridge Lighting

—  Field-earned, not brochure-deep  —

JULY 2026

Prepared for owners, facility teams, consulting engineers, IT/OT teams and project partners

NIAGARA SUPERVISION · OWNER ADVOCACY · SUPPORTABLE FIELD CONTROL

# Three different jobs in one connected-building strategy

These products complement one another because they solve different problems. Keeping the roles distinct makes the system easier to secure, commission and support.

| TECHNOLOGY | PRIMARY JOB | SITS WHERE | DOES NOT REPLACE |
| --- | --- | --- | --- |
| NiagaraMods Reflow | Operator experience | Inside Niagara | Native controller programming |
| Neeve AI | Secure identity and access | At the OT access boundary | BAS hardening or backups |
| Blue Ridge M3 | Lighting control | BACnet-connected field system | Electrical design or code compliance |

## Combined conceptual stack

| PEOPLE Authorized users Operators · vendors | → | ACCESS Neeve AI Identity · policy | → | EXPERIENCE Reflow Responsive UI | → | SUPERVISORY Niagara N4 Integration | → | SYSTEMS Controls + lighting BACnet field layers |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

This is a responsibility model, not a literal single-path wiring diagram. Each project's security and network design must be developed with the owner's IT/OT stakeholders.

UCS DEPLOYMENT STANDARD UCS purchases an appropriate NiagaraMods Reflow project license for each Reflow deployment. Graphics are organized around equipment, operator decisions and service workflows—not decoration.

# NiagaraMods Reflow

UCS partner and standard Niagara operator interface.

## Conceptual role in the architecture

| PEOPLE Operators Desktop · mobile | → | EXPERIENCE Reflow Dashboards · views | → | PLATFORM Niagara N4 Security · station | → | INTEGRATION Drivers BACnet · systems | → | FIELD Controllers Equipment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Current published requirements identify Niagara N4.6+; confirm the exact Reflow and Niagara versions at project start.

## Value and boundaries

| WHERE IT IS STRONG - Responsive operator experience across desktop and mobile. - Equipment views, histories, alarms, schedules and point actions. - Runs inside the owner's Niagara strategy. - Licensed project-by-project by UCS. | DESIGN CONSIDERATIONS - Good graphics still depend on correct points, tags, sequences and naming. - Native controller engineering remains outside Reflow. - Version compatibility must be confirmed before upgrades. - Operator workflow needs discovery; a template alone is not a finished user experience. |
| --- | --- |

ROLE CLARITY Reflow is the experience layer. Niagara remains the supervisory platform, and native controller tools remain responsible for field logic.

Manufacturer references: niagaramodules.com/products/reflow and /products/reflow/tech-specs

# Neeve AI

Zero-trust identity, policy and secure-edge access around the operational-technology network.

## Conceptual role in the architecture

| PEOPLE Authorized users Staff · vendors | → | POLICY Neeve identity Roles · audit | → | TRANSPORT Outbound TLS Controlled path | → | EDGE Secure Edge / Link OT boundary | → | OPERATIONS Niagara + BAS Protected network |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Inline, behind or controlled-path placements create a stronger enforcement point than a device installed merely beside a controls network.

## Value and boundaries

| WHERE IT IS STRONG - OT-focused zero-trust access model. - Central identity, policy and audit context. - Can reduce broad VPN exposure. - Supports governed multi-site remote service. | DESIGN CONSIDERATIONS - Requires early IT routing and identity coordination. - Architecture must prevent bypass of the secure path. - Outbound connectivity and recurring service are operating dependencies. - Does not replace Niagara hardening, backups or network segmentation. |
| --- | --- |

ROLE CLARITY Neeve governs who and what may reach the OT environment. Niagara and Reflow still operate the building.

Manufacturer references: neeve.ai; docs.neeve.ai/docs/deployment-architecture; neeve.ai/product-selector

# Blue Ridge Lighting Solutions

Blue Ridge Technologies M3 lighting control integrated with Niagara through native BACnet.

## Conceptual role in the architecture

| PEOPLE Facility teams Shared operations | → | EXPERIENCE Reflow Useful lighting views | → | SUPERVISORY Niagara N4 Schedules · context | → | LIGHTING Blue Ridge M3 BACnet control | → | FIELD CANbus I/O Sensors · loads |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Final architecture must meet electrical code, listing requirements, emergency-lighting rules and the defined electrical/BAS division of work.

## Value and boundaries

| WHERE IT IS STRONG - Native BACnet integration. - Modular M3 architecture. - Can coordinate schedules and occupancy with HVAC. - Retrofit options can reduce disruption. | DESIGN CONSIDERATIONS - Electrical, lighting and BAS scope boundaries must be explicit. - Expose only points that support an owner workflow. - Commission local lighting and supervisory integration together. - Life-safety, UL and energy-code needs remain project-specific. |
| --- | --- |

ROLE CLARITY Blue Ridge owns purpose-built lighting control. Niagara provides cross-system context and selected supervisory workflows; it does not replace the electrical design.

Manufacturer references: brtint.com/m3_platform and BRT M3 Platform Data Sheet (2024)

# Commissioning and ownership checklist

- Name the system of record for schedules, occupancy commands and alarm acknowledgement.

- Define who owns Niagara, Reflow, Neeve and Blue Ridge licenses and renewal decisions.

- Deliver native source files, station backups, graphics resources, certificates and recovery instructions.

- Test remote access from outside the owner network using the approved identity path.

- Verify local equipment and lighting operation when the supervisory or internet connection is unavailable.

- Document point naming, tags, network addressing, firewall rules and support contacts.

- Train operators on normal use, exception response and who to call before bypassing a security control.

## Responsibility prompts

| USE CASE | FIT | FIELD NOTE |
| --- | --- | --- |
| Operator UI | UCS / Reflow scope | Define pages, actions, trends, alarms and mobile workflows. |
| Remote access | Owner IT + UCS + Neeve | Define identity, approval, routing, logs and break-glass access. |
| Lighting | Electrical + lighting + UCS | Define sequences, local control, BACnet points and commissioning. |

Disclaimer: This document is a conceptual planning aid, not a stamped network, electrical, cybersecurity or controls design. Final architecture must be engineered for the specific project and approved by the owner and responsible design professionals.