UCS TECHNICAL FIELD GUIDE

Niagara Platform Architecture Guide

ABB · Siemens · Honeywell · Johnson Controls

—  Field-earned, not brochure-deep  —

JULY 2026

Prepared for building owners, consulting engineers, facility teams and IT/OT stakeholders

NIAGARA SUPERVISION · OWNER ADVOCACY · SUPPORTABLE FIELD CONTROL

# The UCS point of view

FIELD-EARNED, NOT BROCHURE-DEEP. Our team has installed, programmed and serviced these systems in the field—including lines we do not represent—so we know the real strengths and trade-offs first-hand. That experience lets UCS act as an advocate for the owner, not a salesperson for a badge.

## What stays consistent

- Niagara is the supervisory and integration standard above the controller line.

- NiagaraMods Reflow is the standard UCS operator interface, licensed appropriately for each deployment.

- BACnet helps systems communicate; it does not make controller logic, licenses, databases or service tools interchangeable.

- Native platform engineering tools remain part of a supportable design; one front end does not erase them.

- Controller choice follows the installed base, sequences, IT standards, service resources and owner goals.

## Portfolio-level architecture

| PEOPLE Operators Service teams | → | EXPERIENCE Reflow Responsive UI | → | SUPERVISORY Niagara N4 Alarms · histories | → | AUTOMATION Open BACnet ABB · Siemens · HWE · JCI | → | FIELD Equipment Sensors · actuators |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Conceptual only. Final topologies depend on product generation, software version, licensing, owner cybersecurity standards and existing site conditions.

## How to use this guide

| USE CASE | FIT | FIELD NOTE |
| --- | --- | --- |
| Early design | Compare trade-offs | Use the risers to align owner, engineer, controls and IT expectations. |
| Migration | Inventory first | Do not budget reuse until databases, wiring, firmware, tools and sequences are verified. |
| Selection | Choose the service model | Confirm who can edit native logic, restore backups and support the site after turnover. |

# 01 · ABB Cylon

UCS lead control platform: open BACnet field control beneath Niagara and NiagaraMods Reflow.

## Conceptual Niagara-centered riser

| EXPERIENCE Operators Reflow views | → | SUPERVISORY Niagara N4 Integration | → | IP BACnet/IP Open backbone | → | AUTOMATION CBXi / FLXeon Plant · unitary · VAV | → | FIELD MS/TP · Modbus Sensors · equipment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

ABB logic remains native to CXproHD; Niagara is the owner-facing supervisory and integration layer.

## Field perspective

| WHERE IT IS STRONG - Open BACnet/IP, MS/TP and Modbus paths. - Flexible plant, unitary and VAV controller range. - Native IP terminal options improve service access. - Strong value beneath a Niagara owner standard. | DESIGN CONSIDERATIONS - CXproHD skill and source-file control remain essential. - Mixed Cylon generations require discovery. - Native front-end features may need intentional Niagara rebuilds. - Routing, addressing and controller capacity must be engineered. |
| --- | --- |

## Where it fits

| USE CASE | FIT | FIELD NOTE |
| --- | --- | --- |
| New construction | Best fit | Open-system owners who value flexible field control. |
| Modernization | Strong fit | Preserve useful devices while upgrading supervisory and automation layers. |
| Mixed generations | Discovery first | Inventory databases, logic, wiring and controller models before pricing. |

Owner-advocate question Does the design preserve owner choice at the supervisory layer while keeping controller logic supportable by qualified technicians?

# 02 · Siemens Desigo

New UCS line: Desigo PXC automation integrated into the same Niagara/Reflow operator standard.

NEWLY ADDED LINE UCS-specific Siemens case studies and deep engineering resources will grow as current work is completed. The architecture below is deliberately conservative and does not overstate project history.

## Conceptual Niagara-centered riser

| EXPERIENCE Operators Reflow views | → | SUPERVISORY Niagara N4 Integration | → | SECURE IP BACnet/IP · SC Owner standard | → | AUTOMATION PXC4 / 5 / 7 Native logic | → | FIELD TX-I/O · DXR Rooms · equipment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

ABT Site remains the native engineering environment. BACnet/SC depends on exact versions and certificate-management standards.

## Field perspective

| WHERE IT IS STRONG - Scalable PXC controller family. - BACnet/SC supports secure-network designs. - TX-I/O and phased modernization may preserve viable assets. - Natural fit for an existing Siemens estate. | DESIGN CONSIDERATIONS - Native engineering requires ABT tools and training. - Desigo-native workflows do not all map directly to Niagara. - Legacy APOGEE/TALON reuse must be verified. - UCS project-specific resources are still expanding. |
| --- | --- |

## Where it fits

| USE CASE | FIT | FIELD NOTE |
| --- | --- | --- |
| Existing Siemens | Best fit | Modernize in phases around verified reusable infrastructure. |
| Secure IP | Strong fit | Projects prepared to govern BACnet/SC certificates and networks. |
| Legacy migration | Discovery first | Validate databases, wiring, I/O and controller compatibility. |

Owner-advocate question Which existing Siemens assets still create value, and which reuse assumptions only defer cost or risk?

# 03 · Honeywell Optimizer

Niagara-aligned plant, equipment and VAV control with deliberate IP, T1L and MS/TP choices.

## Conceptual Niagara-centered riser

| EXPERIENCE Operators Reflow views | → | SUPERVISORY Niagara N4 Supervisor | → | INTEGRATION BACnet · FOX Open links | → | AUTOMATION Optimizer Essential · Advanced | → | FIELD IP · T1L · MS/TP VAV · equipment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Confirm current controller availability and exact Niagara/Workbench compatibility during design and again at submittal.

## Field perspective

| WHERE IT IS STRONG - Niagara-based supervisory options. - Broad BACnet, Modbus and integration support. - IP, T1L and MS/TP VAV strategies. - Practical migration paths for mixed installed bases. | DESIGN CONSIDERATIONS - Many generations, tools and licensing models. - Mixed field networks need an explicit service plan. - WEBs, Spyder and CIPer sites require version discovery. - Lifecycle status should be confirmed, not inferred. |
| --- | --- |

## Where it fits

| USE CASE | FIT | FIELD NOTE |
| --- | --- | --- |
| Niagara owners | Best fit | Honeywell hardware beneath one Niagara/Reflow experience. |
| VAV upgrades | Strong fit | IP or T1L may reduce traditional trunk constraints. |
| Legacy estates | Discovery first | Separate controller generations, tools and database access. |

Owner-advocate question Does the selected network type make commissioning and long-term service simpler, or merely move complexity somewhere less visible?

# 04 · Johnson Controls

Facility Explorer and F4 support, with clear separation from Metasys and practical legacy N2 paths.

## Conceptual Niagara-centered riser

| EXPERIENCE Operators Reflow views | → | SUPERVISORY Niagara N4 Open integration | → | SECURE IP BACnet/SC · IP Backbone | → | AUTOMATION CGE · CVE CGM · CVM | → | FIELD MS/TP · N2 XPM · devices |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Facility Explorer and Metasys are related ecosystems, not interchangeable products. Tool, firmware and license details drive the final path.

## Field perspective

| WHERE IT IS STRONG - Facility Explorer is Niagara-based. - BACnet/SC, IP and MS/TP controller options. - Selected N2 paths can support phased migration. - Broad airside equipment-controller range. | DESIGN CONSIDERATIONS - CCT and native source management remain necessary. - FX and Metasys expectations must be separated. - N2 reuse needs device-level verification and an end-state. - IT segmentation and certificates must be engineered. |
| --- | --- |

## Where it fits

| USE CASE | FIT | FIELD NOTE |
| --- | --- | --- |
| FX estates | Best fit | Retain Niagara investment while improving owner experience. |
| N2 transition | Strong fit | Preserve selected devices temporarily during phased work. |
| FX / Metasys mix | Discovery first | Document databases, tools, licenses and feature expectations. |

Owner-advocate question Is the migration plan reducing dependence on legacy tools and trunks each phase, or just wrapping them with a new front end?

# Cross-platform selection matrix

This matrix is a starting point for discovery—not a product scorecard.

| DECISION LENS | ABB | SIEMENS | HONEYWELL | JCI |
| --- | --- | --- | --- | --- |
| UCS positioning | Lead platform | Newly added line | Niagara-aligned | Legacy/FX depth |
| Native tool | CXproHD | ABT Site | Workbench / product tools | CCT / product tools |
| Common strengths | Open BACnet; flexible I/O | PXC scale; BACnet/SC | Niagara alignment; VAV options | FX Niagara; broad controllers |
| Discovery focus | Generations and source files | Legacy reuse and versions | Generations and network types | FX vs Metasys; N2 end-state |
| Owner question | Open and serviceable? | What is truly reusable? | Which network simplifies service? | Does each phase reduce legacy risk? |

## Design and procurement cautions

- Confirm exact model and lifecycle status when the submittal is prepared.

- Define database, license, certificate, backup and source-code ownership in the contract.

- Document IT/OT routing, VLANs, firewall rules, BACnet broadcasts and remote-access responsibilities.

- Test sequences, alarms, histories, trend retention and operator workflows—not just point visibility.

- Treat every reuse claim as a field-verification item until proven.

## Primary public references

| PLATFORM | MANUFACTURER REFERENCE |
| --- | --- |
| ABB CB Line / FLXeon / CXproHD | electrification.us.abb.com/products/building-automation-controls |
| Siemens Desigo PXC / modernization | siemens.com/en-us/products/desigo/pxc and /campaigns/desigo-modernization-pathway |
| Honeywell Optimizer | buildings.honeywell.com — Optimizer Supervisor, Essential, Advanced and VAV pages |
| Johnson Controls Facility Explorer | johnsoncontrols.com/building-automation-and-controls/facility-explorer and docs.johnsoncontrols.com |

Disclaimer: This document is a conceptual planning aid, not a stamped controls design, cybersecurity plan or product-availability guarantee. Final architecture must be engineered for the specific project and approved by the owner and responsible design professionals.